## Sheet1
Questions | Answers
How much more do fixed bottom offshore wind turbines cost when compared to above shore turbines due to the increase in wind, larger size, and heavier duty materials? | There is a small premium on offshore turbines on a $/kW basis because they have to have special corrosion prevention, pressurized nacelles, etc. but the real cost added is in the balance of plant costs. Higher installation costs, higher substructure costs, and higher maintenance costs make offshore costs about 2x the land-based projects. This cost is partially offset in many cases by higher energy production offshore.
How much energy is lost due to the increase in travel distance (ocean vs land)? | Offshore wind plants are close to load so transmission distances are often closer. It is difficult to compare the physical transport distances between land-based and offshore because the logistics are different.
How big a factor is bottom substrate for siting? Are some areas (like silt) unsuitable? | Soft soils make it difficult to install monopiles but allow jacket foundations with no problem. Silt soils may also preclude some other foundation types.
Do some states have policies either encouraging or discouraging offshore wind? Examples? | There are eight states that have aggressive policies to adopt offshore wind MA, RI, CT, NY, NJ, MD, VA, NC. In addition CA, OR, LA, ME, NH, WA, HI are considering policies. The NREL team is not aware of any current policies against. However, historically, there have been state-level offshore wind moratoriums proposed and enacted.
Can the power of the ocean that moves the seabed be harnessed to create a hybrid ocean energy facility? | Based on current research, no cost advantages to making hybrid wind/wave energy facilities have been identified but there could be some options that have not yet been explored.
How far out are turbines clearly visible from shore? | Turbines can be seen from shore in clear weather at 10 to 15 miles. The exact distance at which they vanish depends on the size of the turbine, the weather, the curvature of the earth, etc.
What is the outlook for offshore wind on the Pacific coast? | The Pacific states are looking into offshore wind. The wind resources are very good. The projects will be floating because of the deeper waters. There are 5 call areas combined in CA and HI already.
Are some areas closed due to DOD restrictions? | The DOI and DOD are negotiating to potentially allow offshore wind in areas the DOD has historically identified as off limits.
Slide 13 configuration drawings show "J tubes" -- what is their function? Some of the trade press suggest that the weak link in offshore wind is the cable that connects units within an array and connects the offshore substation with the land grid. Does your experience bear this out? | The J tubes guide the array cables from the turbine to the seabed. Cables failures have comprised the majority of insurance claims in European wind plants. U.S. is developing guidance for best practices under ACP offshore recommended practices for subsea cables under Working Group 5 that hope to avoid these mistakes of the past.
Block Island Wind was scheduled to be taken offline in Spring 2021 to replace a section of high voltage electric transmission cable. Buried depth of the cable was inadequate to protect the cable from seafloor environment. Is the cable replacement completed and Block Island restored to service? What was learned to prevent cable degradation at future offshore wind sites? | BOEM/BSEE and the offshore wind industry currently have teams working on technological standards to address these and other technology based issues. NREL is not aware of the status of repair.
What is limiting offshore wind in the Great Lakes? | The technology for deep water floating systems in ice flow environments has not been proven yet so there is a perceived risk. The biggest problem is that the ocean-based turbines and their installation vessels cannot fit through the locks, so Great Lakes wind turbines will likely be smaller. In addition, states with Great Lakes coastline have not been supportive and east coast deployments have been more attractive for the burgeoning industry. That may be changing in New York waters, where the state is conducting feasibility studies.
Does Block Island Wind have a daily generation pattern? More wind at predictable times of the day? Is hourly generation data available for download? EIA has hourly data for Balancing Authorities, but not individual powerplants. | Yes - but NREL does not have this data.
Are the array cables AC or DC? | The array cables are AC. New projects will likely adopt a 66-kV array cable spec in the near term.
As an alternative to connecting to the onshore grid, are any of the facilities under consideration in the USA using various storage technologies to "ship" to shore? | Not yet, but future technology projections suggest that we may have battery and H2 storage that can help offset the export cable requirements.
What is the decommissioning plan of the offshore wind turbines? Will there be thousands of WTG skeletons up and down the coast in 40 years, or is a decommissioning/repowering part of the development plan requirements in the regulations process? | Decommissioning is part of the upfront permitting process. Developers need to have a plan, and a security bond is held to pay for decommissioning at end of life.
What is NREL doing to address the workforce needed to fill all the jobs that offshore wind will create? | NREL has a wind workforce team and several projects looking to understand and help build the offshore wind workforce pipeline.
What is the magnet technology (Superconducting or Permanent magnet - based) used in the GE Machines? | GE machines currently use permanent magnets; superconducting generators are possible for future turbine technology.
What is the estimated lifetime of a typical turbine? | Today the life of an offshore wind plant is designed to be about 25 years. However, life extension is a major topic.
You cited technical potential capacity of 11.6 GW for existing 16 leases that seems quite low. I have seen numbers that put it closer to 25 GW. Can you expand on where you are getting that technical capacity estimate? | The technical capacity estimate of 11.6 GW includes the leases that have not committed to specific project plans.
What environmental studies have been done to mitigate adverse effects to wildlife? | There are many environmental studies on the effects of offshore wind energy on wildlife and potential mitigation measures/technology. We have provided several links to resources where these studies can be found: DOE Wind Energy Technologies Office environmental research: https://www.energy.gov/eere/wind/environmental-impacts-and-siting-wind-projects BOEM Renewable Energy Research: https://www.boem.gov/environment/environmental-studies/renewable-energy-research Tethys database: https://tethys.pnnl.gov/knowledge-base-wind-energy California Energy Commission Offshore Wind Research and Development Database: https://www.energy.ca.gov/sites/default/files/2020-06/Offshore_Wind_Research_and_Development_Database_ada.xlsx
With the larger size turbines, what are the challenges that you see with foundation design beyond installation? | Fabrication is a big challenge due to an immature supply chain and high capital costs to set up new factories. As water depths get deeper, different foundations will be used. Floating foundations appropriate for these deeper waters require innovations in platform design, fabrication, and operation. Due to large component sizes, componentsmust be made close to shore and shipped over water.
You mentioned that array cable costs and turbine spacing are important to balance for wind farm planning. Do you think there may be an upper limit on turbine size related to this spacing challenge & array cable costs? | No, NREL researchers do not see an upper limit that is defined by cable constraints or spacing - but there will be a push to increase the voltage of array cables (120kV in the future) to allow more large turbines to operate on a string.
Can you discuss corrosion protection for the foundations? | Corrosion is managed using the best practices of the oil and gas industry. There are several standards that can be references in ACP OCRP-1 that is under review.
What is planned as far as recycling parts to the turbines when the life of the product runs out? | Most parts are recyclable, retrofittable, or reusable. Blades are a big challenge but there have been several advances toward sustainable/recyclable blades recently (re. Vestas). DOE and NREL are currently researching ways to recycle existing wind turbine blades, and different materials and processes that can be used on future blades to increase recyclability.
What advantages does the use of concrete foundations provide over steel foundations? | Concrete has a higher tolerance to corrosion and is thought to be more adaptable to domestic supply chains.